u7ide Getting Started

– Creating a new project

– Start program u7;

– Go to to “Project” tab page (this is default tab page, if program is just started it is not required step) then click button “New Project..”, the window “Create New Project” will appear;

– Enter desired project name, template is [CUSTOMER]_[UNIT][SYSTEM][NO]. Example: project name is KZNPP_6SDS1, customer Kozloduy Nuclear Power Plant (KZNPP), Unit 6, Shut Down System 1 (SDS1);

– Enter and confirm password for user Administrator, in case of too weak password the system will prompt to enter another password;

– Press “Ok”, the new project will be created, it will be upgraded to the latest version and will appear in the project list;

– Opening project

– To open project, click on it and press “Open Project” button (or double click on project in the project list), the program will ask to enter username and password;

– In the field “Username” enter “Administrator”, fill the password section with the pointed password during creation steps (user “Administrator” is automatically created during initializing of a new project);

– Press “OK”, in case of correct data the project will be opened and main window will change its caption to “u7 - kznpp_sds1 - Administrator”;

– Hardware Configuration (will be renamed to Equipment Configuration later)

– Go to “Hardware Configuration” tab page, work area of this tab page consists of Object Tree (left side) and Property Grid (right side);

– Any project must contain at least one system, to add a system left click on Object tree, select “Add Object –> System” from the context menu, the new system will be added;

– Any object has identifier (StrID), the new system is created with the default StrID “SYSTEMID”, change it to a desired one (for example SDS1 for Shut Down System 1), to change any object's property press on object, press on a property value, enter a new value, press Enter;

– Change system caption (for example: Shut Down System 1) ;

– Add rack to the system, right click on the system, select “Add Obejct → Rack”, the new rack will be added;

– Set StrID for the new rack, for instance “$(PARENT)_RCH0”. Note – some property fields may contain macroses like “$(PARENT)”, it means that during building process this part of the value will be changed to corresponding value, thus StrID value ”$(PARENT)_RCH0” becomes “SDS1_RCH0” as the parent for the rack is system with StrID “SDS1”;

– Set Caption for the new rack, for instance “SDS Rack”;

– Add Chassis to rack, right click on rack, select “Add Object → Chassis”, set StrID and Caption for chassis, for instance “$(PARENT)_CHS”;

– At this moment everything is ready for adding modules to chassis, it is considered that chassis should contain next modules:
Place 0: LM-1 (Logic Module);
Place 1: DIM (Discrete Input Module);
Place 2: DOM (Discrete Output Module);
Place 3: AIM (Analogue Input Module);
Place 4: AOM (Analogue Output Module);

– To add module to chassis, select chassis, right click on it and select “Add From Preset → Preset Module”, select module “LM-1” from the list, set field “Place” to 0 for this module;

– Set property “Channel“ for module LM-1 to value 1;

– Add module DIM, set field “Place“ to 1;
– Add module DOM, set field “Place“ to 2;
– Add module AIM, set field “Place“ to 3;
– Add module AOM, set field “Place“ to 4;

– At this point minimum hardware configuration is done, project contains:
system SDS1;
rack SDS1_RCH0;
chassis SDS1_RCH0_CHS;
module SDS1_RCH0_CHS_MD00 (LM-1);
module SDS1_RCH0_CHS_MD01 (DIM);
module SDS1_RCH0_CHS_MD02 (DOM);
module SDS1_RCH0_CHS_MD03 (AIM);
module SDS1_RCH0_CHS_MD04 (AOM);

– To add inputs from module DIM to Application Signals right click on DIM and choose “Inputs/Outputs to signal”, this operation will add Application Signals connected to modules inputs or outputs;

– Go to “Application Signals” tab page, press Refresh button, the list of signals which can be used for drawing Application Logic Schemes will be shown, besides inputs and outputs list contains validity signals for them;

– Go back to “Hardware Configuration” tab page and perform operation of adding application signals for modules DOM, AIO, AOM (left click on module and choose “Inputs/Outputs to signal”);

– Application Signals

– Go to “Application Signals” tab page, press Refresh button, the list of added signals will be shown, added signals have acceptable default value;

– Application Logic Schemes

– Go to “Application Logic” tab page, it has control tab page and schemes list (empty now);

– Right click on scheme list control, select “Add File...”, set file name (Exaple: testlogic) and press “OK”;

– Program will ask to set scheme properties, set “StrID” to #TESTLOGIC, set field “Caption” to “Test Logic”, press OK, the new Logic Scheme will be added to the list;

– To open scheme for editing it must be checked out for edit, as it is just created it is in state Checked Out;

– To open scheme double click it on list, the new tab with the empty scheme will be opened, it will have caption “#TESTLOGIC” which is the schemes StrID;

– All Application Logic Schemes must be tied up to specific Logic Modules (LM-1) where this logic will be executed, this is done by setting “HardwareStrIDs” property for Logic Scheme;

– To set up link between Application Logic Scheme and Logic Module, right click on Logic Scheme drawing area, select “File → Properties...”, set property “HardwareStrIDs” to Logic Module StrID (SDS1_RCH0_CHS_MD00);

– At this point everything is ready to draw Application Logic, any logic should contain input and output signals, logic elements and links, in the next steps simple logic scheme with two inputs, logic “AND” and output will be created;

– To add input item, right click on scheme, select “Add Item → Input”, put item on scheme;

– For all input and output items must be assigned Application Signal, select Input item, right click on it, select “Properties...”, set property “StrIDs” to “#SDS1_RCH0_CHS_MD01_CTRLIN_INH01A”, what is input 1 for DIM module;

– Scheme navigation tips:
To Zoom In/Zoom Out, use mouse wheel or press Ctrl + Plus, Ctrl + Minus;
To adjust scheme position while it is zoomed in, press and hold mouse wheel and move it;
To copy item, select it and drag it with pressed Ctrl;

– Add one more Input item and set ”StrIDs“ for it to “#SDS1_RCH0_CHS_MD01_CTRLIN_INH02A” what is input 2 for DIM module;

– Add logical “AND” item, right click on scheme, select “Add Item → FBL Element”, Select “and_v1” from the logical element list, press “OK”, put item on scheme;

– Connect pins between items with Link, right click on scheme, select “Add Item → Link”, press and hold left mouse button on one pin, move mouse to the destination pin, release button, to set custom link path do not releasing left button do right click;
– Add Output item, set “StrIDs” fro it to “#SDS1_RCH0_CHS_MD02_CTRLOUT_OUT01”, what is discrete output 1 in module DOM;

– Link output item to logical “and_v1” output pin;

– Save Scheme with Ctrl + S;

– Building Project

– Go to “Build” tab page, press “Build” button;

– Build will be started, output log window will show the build process;

– All warning messages have orange colour, error messages re red;

– Build process should be done with the only warning which inform that in case of Debug build, workcopies of files can be used instead of fixed changes;

– The result of build is a set of output files:
Application Logic files;
Module Configuration files;
Reports;
Log file;
etc.

– Application Logic and Module Configuration can be written to Logic Module, after start this module executes new logic which was drawn in Application Logic Scheme editor;